SAMPLE SPECIFICATION

Air Valves for Clean Water

GA-H2OAV-SPEC Rev A

1.0	GENERAL

1.1	Manufacturer shall have a minimum of ten (10) years’ experience in the manufacture of automatic air valves.

1.2	Manufacturer shall have an ISO-9001 quality management system certified by an accredited body.

1.3	When requested, the manufacturer shall provide detailed product data and descriptive literature including dimensions, weight, capacity, pressure rating, materials of construction and cross-sectional drawings clearly illustrating the individual components.

1.4	All air valves shall meet or exceed the requirements of AWWA Standard C512 (latest revision).

1.5	Air valves used on potable water shall be NSF-61 certified for contact with drinking water and NSF-372 certified lead free.

2.0	AIR VALVES FOR CLEAN WATER

2.1	Construction: Air release, air & vacuum and combination air valve body and cover shall be cast iron per ASTM A126 Class B, lined and coated with NSF-61/600 certified epoxy.  The float(s), orifice and internal linkage mechanisms shall be 316 stainless steel, non-metallic components are not acceptable.  The float(s) shall be rated for a minimum of 750 PSI collapse pressure.  Rubber components shall be Buna-N.  Cover bolts and nuts shall be [A307 zinc plated steel] [316 stainless steel] (Specifier to select).  Sizes 3-inch and smaller shall have an NPT pipeline connection and be rated for 300 PSI, 4-inch and larger shall have a flanged pipeline connection per ANSI/ASME B16.1 Class 125 rated for 200 PSI or Class 250 rated for 300 PSI.

2.2	Air Release Valves:

2.2.1	Provide the valve with an orifice suitable for [150 PSI] [300 PSI] maximum working pressure. (Specifier to select)

2.2.2	Specify when required: Provide the valve with a vacuum check to prevent air re-entry.

2.3	Air & Vacuum Valves: Sizes 4-inch and smaller shall have an NPT outlet connection.  The outlet of 6-inch and larger valves shall have [a protective cowl] [an ANSI Class 125 flange connection].  (Specifier to select)

2.3.1	The valve shall have the same size inlet and outlet, and the venting orifice shall be no smaller than inlet connection size.

2.4	Air & Vacuum Valves for Vertical Turbine Pumps: Valves shall conform to paragraphs 2.1 and 2.3, but 3-inch and smaller sizes shall be provided with a double-acting throttle device for field adjusting the air discharge rate and 4-inch and larger shall be provided with an anti-slam surge check with adjustable orifices.

Page 1 of 2

2.5	Combination Air Valves: Combination air valves shall provide the functions of an air & vacuum and an air release valve, either in a single body or an air & vacuum valve with an externally mounted air release valve.  Either configuration shall meet the requirements of preceding paragraphs.

2.5.1	Provide an air release orifice suitable for up to [150 PSI] [300 PSI] working pressure. (Specifier to select)

2.6	Vacuum Breaking Valves: Valves shall be full ported for vacuum relief with an ANSI Class 125 or 250 flanged pipeline connection and a screened air inlet to protect against the entry of debris.  The plug and seat shall be lead free bronze or 316 stainless steel with a Buna-N or EPDM rubber seal.

2.6.1	Specify when required: The valve shall be provided with an externally mounted air release valve with an orifice suitable for [150 PSI] [300 PSI] maximum working pressure.  (Specifier to select)

3.0	MANUFACTURER

3.1	Clean water air valves shall be GA Industries Series 900, manufactured by VAG USA, LLC, Mars, PA USA.

Page 2 of 2