SAMPLE SPECIFICATION

DUROVENT All Stainless Steel Air Valves for Sewage and Wastewater

GA-900SS-SPEC Rev A

1.0	GENERAL

1.1	Manufacturer shall have a minimum of ten (10) years’ experience in the manufacture of automatic air valves.

1.2	Manufacturer shall have an ISO-9001 quality management system certified by an accredited body.

1.3	When requested, the manufacturer shall provide detailed product data and descriptive literature including dimensions, weight, capacity, pressure rating, materials of construction and cross-sectional drawings clearly illustrating the individual components.

1.4	All air valves shall meet or exceed the requirements of AWWA Standard C512 (latest revision).

2.0	AIR VALVES FOR SEWAGE AND WASTEWATER

2.1	Construction: Air release, air & vacuum and combination air valve body and cover shall be Type 316 stainless steel per ASTM A351 Grade CF8M.  The body shall be elongated to minimize fouling and spillage.  The float(s), orifice, plug, seat and internal linkage mechanisms shall be 316 stainless steel, non-metallic components are not acceptable.  The float(s) shall be rated for a minimum of 750 PSI collapse pressure.  Rubber components shall be Buna-N.  Cover bolts, nuts and pipe plugs shall be 316 stainless steel.

2.1.1	(Specify when required) Standard Backflushing Attachments: Provide each air valve with an inlet isolating bronze ball valve, ½-inch bronze flushing ball valve, 1-inch bronze blow off ball valve, quick connect couplings and a minimum of 5 feet of rubber hose.

or

2.1.1	(Specify when required) Durovent Backflushing Attachments: Provide each air valve with an inlet isolating 316SS ball valve, ½-inch 316SS flushing ball valve, 1-inch 316SS blow off ball valve, 316SS quick connect couplings and a minimum of 5 feet of rubber hose.

2.2	Air Release Valves: Valve shall have a 2-inch NPT pipeline connection and a ½-inch NPT outlet connection.

2.2.1	Provide the valve with an orifice rated for [75 PSI] [150 PSI] maximum working pressure. (Specifier to select)

2.2.1	Specify when required: The valve shall have a “short” body not exceeding 12 inches to accommodate shallow cover installations.

2.2.3	Specify when required: Provide the valve with a bronze vacuum check to prevent air re-entry.

2.3	Air & Vacuum Valves: Valve shall be 1-inch or 2-inch size with NPT pipeline connection for up to 200 PSI working pressure.  The venting orifice shall be no smaller than nominal valve size.  The inlet and outlet connections shall be the same size except 1-inch valves shall have a 2-inch pipeline connection to minimize clogging.

2.3.1	Specify when required: Sizes 2-inch and smaller shall have a “short” body not exceeding 12 inches to accommodate shallow cover installations.

Page 1 of 2

2.4	Combination Air Valves: Combination air valves shall be either single body or dual body (an air & vacuum valve with an externally mounted air release valve).  Either configuration shall meet the requirements of preceding paragraphs.

2.4.1	Specify when required: Dual body combination air valve in sizes 2-inch and smaller shall be short body with an overall height not exceeding 12 inches.

2.4.2	Dual body valves shall have a 316SS isolating ball valve between the air release and air & vacuum valves.

2.4.3	Provide the combination air valve with an air release orifice rated for [75 PSI] [150 PSI] maximum working pressure. (Specifier to select)

3.0	MANUFACTURER

3.1	Durovent all stainless steel sewage and wastewater air valves shall be GA Industries Series 900SS as manufactured by VAG USA, LLC, Mars, PA USA.

Page 2 of 2