SAMPLE SPECIFICATION

Silent Check Valves

GA-SCV-SPEC Rev B

1.0	GENERAL

1.1	Manufacturer shall have a minimum of ten (10) years’ experience in the manufacture of silent check valves.

1.2	Manufacturer shall have an ISO-9001 quality management system certified by an accredited body.

1.2	When requested, detailed product data and descriptive literature including dimensions, weight, capacity, pressure rating, materials of construction and cross-sectional drawings clearly illustrating the individual components.

2.0	PRODUCT

2.1	Globe style valves shall be 300 PSI rated with integral flat-faced flanged connections conforming to ANSI Class 125/150 or 250/300. Wafer style valves sizes 2-inch through 6-inch shall be 500 PSI rated and designed to fit between ANSI Class 125/150/250/300 flanges.  Sizes 8-inch and 10-inch shall be 300 PSI rated and fit between ANSI Class 125/150 flanges.

2.2	The valve design shall be of the in-line type that initiates valve closure as soon as the forward flow velocity decreases and is fully closed before flow reversal to prevent water hammer.

2.3	The valve shall have a spring-loaded, center-guided disc that presents a concave surface to the flow allowing the valve to fully open at minimum velocity and a short stroke for quick closure.

2.4	When fully open, the flow area through the valve shall be no less than the internal area of the nominal pipe size.  Valve design shall permit installation in a horizontal or vertical flow up pipe without modification.

2.5	The valve shall be metal-to-metal or EPDM to metal seated [Specifier to select]. The valves shall not exhibit more than the allowable leakage when tested according to Section 5 of AWWA Standard C508.  EPDM to metal seated valves shall incorporate an EPDM rubber O-ring retained in a dovetail groove without bonding to provide zero leakage at both high and low pressure with a metal-to-metal back up to prevent over compression.

2.6	All components shall be field replaceable using common tools.

3.0	MATERIALS

3.1	The valve body shall be fusion bond epoxy lined and coated ductile iron conforming to ASTM A536 Grade 65-45-12

3.2	The valve disc and seat ring shall be Alloy C87600 or C87800 lead-free bronze

3.3	The internal spring shall be Type 302 stainless steel and the disc guide shall be Alloy C95400 lead- free bronze.

4.0	MANUFACTURER

4.1	Silent check valves shall be GA Industries Figure F280 (globe) or F290 (wafer).